{"text_format":"3","workbook":"xlsx","n_sheets":4,"sheets":["开关阀","调节阀","开关阀 (技术)","调节阀 (技术)"],"not_rendered":{"images":2,"external_links":5,"defined_names":217},"read":"whole","date_system":"1900"}

{"sheet":"开关阀","index":0,"n_rows":37,"n_cols":15,"rows_kept":37,"merged":[[0,0,0,14],[1,0,1,14],[2,0,2,14],[31,2,31,3],[31,4,31,8],[32,2,32,3],[32,4,32,8],[33,2,33,3],[33,4,33,8],[34,2,34,3],[34,4,34,8],[35,2,35,3],[35,4,35,8],[36,0,36,12]]}
["晨鸣集团备件询价单"]
["*请注明报价币种（如果人民币报价，需含13%税、含到各晨鸣子公司运费）*   *报价3天之内回传，谢谢*    *包装方式严格按照行业标准*"]
["联系人：李军辉   电话：0536-2158712 传真：0536-2156381   E-mail:965143914@qq.com"]
["序号","提报公司","仪表位号","应 用","介质","管径","回路图编号","单位","数量","单价","总价","品牌","产地","货期","承诺寿命"]
[1,"黄冈","221HV-6008","节子洗涤器平衡水阀","稀黑液",25,"HV-001-DCS-JB-JB-XX","台",1]
[2,"黄冈","221HV-6010","节子洗涤器集渣阀","节子",150,"HV-001-DCS-JB-JB-XX","台",1]
[3,"黄冈","221HV-6012","节子洗涤器排渣阀","节子",150,"HV-001-DCS-JB-JB-XX","台",1]
[4,"黄冈","221HV-6015","节子洗涤器冲洗水阀","稀黑液",25,"HV-001-DCS-JB-JB-XX","台",1]
[5,"黄冈","221HV-6103","浆渣洗涤器集渣阀","尾浆",150,"HV-001-DCS-JB-JB-XX","台",1]
[6,"黄冈","221HV-6104","浆渣洗涤器平衡水阀","滤液",25,"HV-001-DCS-JB-JB-XX","台",1]
[7,"黄冈","221HV-6106","浆渣洗涤器冲洗水阀","稀黑液",25,"HV-001-DCS-JB-JB-XX","台",1]
[8,"黄冈","221HV-6107","浆渣洗涤器排渣阀","尾浆",150,"HV-001-DCS-JB-JB-XX","台",1]
[9,"黄冈","221HV-6111","除砂器1平衡水阀","稀黑液",25,"HV-001-DCS-JB-JB-XX","台",1]
[10,"黄冈","221HV-6114","除砂器1排气阀","稀黑液",25,"HV-001-DCS-JB-JB-XX","台",1]
[11,"黄冈","221HV-6116","除砂器2平衡水阀","稀黑液",25,"HV-001-DCS-JB-JB-XX","台",1]
[12,"黄冈","221HV-6119","除砂器2排气阀","稀黑液",25,"HV-001-DCS-JB-JB-XX","台",1]
[13,"黄冈","241HV-6303","EOP段喂料中浓泵、真空泵密封水阀","密封水",25,"HV-001-DCS-JB-JB-XX","台",1]
[14,"黄冈","241HV-6310","EOP段喂料立管过氧化氢开关阀","过氧化氢",25,"HV-001-DCS-JB-JB-XX","台",1]
[15,"黄冈","241HV-6319","蒸汽浆料加热器蒸汽阀1","中压蒸汽",65,"HV-001-DCS-JB-JB-XX","台",1]
[16,"黄冈","241HV-6320","蒸汽浆料加热器蒸汽阀2","中压蒸汽",65,"HV-001-DCS-JB-JB-XX","台",1]
[17,"黄冈","241HV-6333","蒸汽浆料加热器蒸汽阀3","中压蒸汽",65,"HV-001-DCS-JB-JB-XX","台",1]
[18,"黄冈","241HV-6334","蒸汽浆料加热器蒸汽阀4","中压蒸汽",65,"HV-001-DCS-JB-JB-XX","台",1]
[19,"黄冈","241HV-6324","Eop段氧气加入器氧气开关阀","氧气",25,"HV-001-DCS-JB-JB-XX","台",1]
[20,"黄冈","241HV-6325","Eop段化学品混合器出口阀","EOP段浆",250,"HV-001-DCS-JB-JB-XX","台",1]
[21,"黄冈","241HV-6341","Eop反应塔布料器进料阀1","EOP段浆",200,"HV-001-DCS-JB-JB-XX","台",1]
[22,"黄冈","241HV-6342","Eop反应塔布料器进料阀2","EOP段浆",200,"HV-001-DCS-JB-JB-XX","台",1]
[23,"黄冈","241HV-6343","Eop反应塔布料器进料阀3","EOP段浆",200,"HV-001-DCS-JB-JB-XX","台",1]
[24,"黄冈","241HV-6344","Eop反应塔布料器进料阀4","EOP段浆",200,"HV-001-DCS-JB-JB-XX","台",1]
[25,"黄冈","241HV-6345","Eop反应塔卸料器密封水阀控制","密封水",15,"HV-001-DCS-JB-JB-XX","台",1]
["备注：具体详细数据见技术协议",null,null,"签订联系人：杨主任：13793690068",{"$nulls":6},{"$f":"SUM(K5:K29)","v":0}]
[]
[null,null,"报价单位："]
[null,null,"付款方式：",null,"货到票到90天付90%；10%质保一年（财司票）"]
[null,null,"联系人："]
[null,null,"联系方式:"]
[null,null,"注册资金："]
["报价单位必须为发票（13%增值税专票）开具单位及结算单位；请务必于两日内回复。"]

{"sheet":"调节阀","index":1,"n_rows":45,"n_cols":15,"rows_kept":45,"merged":[[0,0,0,14],[1,0,1,14],[2,0,2,14],[39,2,39,3],[39,4,39,8],[40,2,40,3],[40,4,40,8],[41,2,41,3],[41,4,41,8],[42,2,42,3],[42,4,42,8],[43,2,43,3],[43,4,43,8],[44,0,44,12]]}
["晨鸣集团备件询价单"]
["*请注明报价币种（如果人民币报价，需含13%税、含到各晨鸣子公司运费）*   *报价3天之内回传，谢谢*    *包装方式严格按照行业标准*"]
["联系人：李军辉   电话：0536-2158712 传真：0536-2156381   E-mail:965143914@qq.com"]
["序号","提报公司","仪表位号","应 用","介质","口径","回路图编号","单位","数量","单价","总价","品牌","产地","货期","承诺寿命"]
[1,"黄冈","221LCV-6005","节子洗涤器液位调节阀","尾浆",250,"CV-001-DCS-JB-JB-XX","台",1]
[2,"黄冈","221HCV-6006","筛选喂料泵来浆稀释调节阀","稀黑液",100,"CV-001-DCS-JB-JB-XX","台",1]
[3,"黄冈","221FCV-6014","节子洗涤器稀释调节阀","稀黑液",150,"CV-001-DCS-JB-JB-XX","台",1]
[4,"黄冈","221PCV-6017","压力除节机进浆压力调节阀","粗浆",300,"CV-001-DCS-JB-JB-XX","台",1]
[5,"黄冈","221FCV-6020","压力除节机尾浆出口流量调节阀","尾浆",125,"CV-001-DCS-JB-JB-XX","台",1]
[6,"黄冈","221FCV-6021","压力除节机稀释流量调节阀","稀黑液",80,"CV-001-DCS-JB-JB-XX","台",1]
[7,"黄冈","221HCV-6022","压力除节机冲洗流量调节阀","稀黑液",80,"CV-001-DCS-JB-JB-XX","台",1]
[8,"黄冈","221FCV-6087","压力除节机、一段压力筛进浆流量调节阀","浆",350,"CV-001-DCS-JB-JB-XX","台",1]
[9,"黄冈","221FCV-6091","一段压力筛稀释流量调节阀","稀黑液",100,"CV-001-DCS-JB-JB-XX","台",1]
[10,"黄冈","221FCV-6093","一段压力筛尾浆流量调节阀","尾浆",150,"CV-001-DCS-JB-JB-XX","台",1]
[11,"黄冈","221FCV-6094","二段压力筛进浆流量调节阀","尾浆",300,"CV-001-DCS-JB-JB-XX","台",1]
[12,"黄冈","221PCV-6095","二段压力筛进浆压力调节阀","浆",300,"CV-001-DCS-JB-JB-XX","台",1]
[13,"黄冈","221FCV-6098","二段压力筛稀释流量调节阀","稀黑液",65,"CV-001-DCS-JB-JB-XX","台",1]
[14,"黄冈","221FCV-6100","二段压力筛尾浆流量调节阀","尾浆",125,"CV-001-DCS-JB-JB-XX","台",1]
[15,"黄冈","221LCV-6108","浆渣洗涤器液位调节阀","尾浆",200,"CV-001-DCS-JB-JB-XX","台",1]
[16,"黄冈","221FCV-6109","浆渣洗涤器稀释调节阀","稀黑液",125,"CV-001-DCS-JB-JB-XX","台",1]
[17,"黄冈","221PDCV-6115","三段压力筛上浆回流压力调节阀","尾浆",65,"CV-001-DCS-JB-JB-XX","台",1]
[18,"黄冈","221FCV-6120","三段压力筛出浆流量调节阀","尾浆",200,"CV-001-DCS-JB-JB-XX","台",1]
[19,"黄冈","221PCV-6121","三段压力筛进浆压力调节阀","尾浆",250,"CV-001-DCS-JB-JB-XX","台",1]
[20,"黄冈","221FCV-6124","三段压力筛尾浆流量调节阀","尾浆",100,"CV-001-DCS-JB-JB-XX","台",1]
[21,"黄冈","221FCV-6126","三段压力筛稀释流量调节阀","稀黑液",65,"CV-001-DCS-JB-JB-XX","台",1]
[22,"黄冈","221HCV-6127","稀释水泵出口调节阀","稀黑液",350,"CV-001-DCS-JB-JB-XX","台",1]
[23,"黄冈","241HCV-6301","Eop喂料立管下部稀释调节阀","滤液",80,"CV-001-DCS-JB-JB-XX","台",1]
[24,"黄冈","241HCV-6302","Eop喂料立管上部稀释调节阀","滤液",50,"CV-001-DCS-JB-JB-XX","台",1]
[25,"黄冈","241HCV-6311","Eop段喂料中浓泵出口调节阀","浆","200/250","CV-001-DCS-JB-JB-XX","台",1]
[26,"黄冈","241FCV-6314","进Eop喂料立管氢氧化钠流量调节阀","氢氧化钠",40,"CV-001-DCS-JB-JB-XX","台",1]
[27,"黄冈","241FCV-6315","进Eop喂料立管过氧化氢流量调节阀","过氧化氢",25,"CV-001-DCS-JB-JB-XX","台",1]
[28,"黄冈","241FCV-6316","蒸汽浆料加热器蒸汽总管流量调节阀","中压蒸汽",100,"CV-001-DCS-JB-JB-XX","台",1]
[29,"黄冈","241FCV-6323","Eop段氧气加入器氧气总管流量调节阀","氧气",25,"CV-001-DCS-JB-JB-XX","台",1]
[30,"黄冈","241HCV-6330","Eop反应塔顶部滤液阀","滤液",80,"CV-001-DCS-JB-JB-XX","台",1]
[31,"黄冈","241PCV-6331","Eop反应塔顶部压力调节阀","浆",250,"CV-001-DCS-JB-JB-XX","台",1]
[32,"黄冈","241FCV-6336","Eop喷放塔滤液流量调节","滤液",250,"CV-001-DCS-JB-JB-XX","台",1]
[33,"黄冈","241QCV-6340","Eop喷放塔中浓泵出口浓度","滤液",125,"CV-001-DCS-JB-JB-XX","台",1]
["备注：具体详细数据见技术协议",null,null,"签订联系人：杨主任：13793690068",{"$nulls":6},{"$f":"SUM(K5:K37)","v":0}]
[]
[null,null,"报价单位："]
[null,null,"付款方式：",null,"货到票到90天付90%；10%质保一年（财司票）"]
[null,null,"联系人："]
[null,null,"联系方式:"]
[null,null,"注册资金："]
["报价单位必须为发票（13%增值税专票）开具单位及结算单位；请务必于两日内回复。"]

{"sheet":"开关阀 (技术)","index":2,"n_rows":36,"n_cols":35,"rows_kept":36,"merged":[[8,0,9,0],[8,1,9,1],[8,2,8,9],[8,10,8,17],[8,19,8,21],[8,22,8,24],[8,25,8,26]]}
{"$rows_empty":8}
["Tag No.","Application","Process Data\n工艺参数 ",{"$nulls":7},"Valve Information\n阀门信息",{"$nulls":8},"Solenoid Valve\n电磁阀",null,null,"Limit Switch\n限位开关",null,null,"Press. Data\n压力参数(KPa)"]
[null,null,"Medium","Size\nmm","Class\nPN","Pipe\nMater.","Temp.\n℃","Press.\nKPa","Flow\nm3/h","Dens.\nKg/dm3","Valve\nType","Size\nmm","Class\nPN","Body\nMater.","Spool\nMater.","Seat\nMater.","Conn.\nType","Fail\nType","Act.\nType","Type","Power","Air Supply\n(KPa)","Open\nL.S.","Close\nL.S.","Type","Inlet\nPress.","dP\nColsed","Sup.","Remarks","Rev.",null,"回路图编号"]
["仪表位号","应 用","介质","管径","压力\n等级","管道\n材质","温度","压力","流量","密度","类型","口径","压力\n等级","阀体\n材质","阀芯\n材质","阀座\n材质","连接\n形式","故障\n类型","执行器\n类型","类型","电源","气源","开限位","关限位","类型","进口\n压力","关断\n压差","供货","备注","版本"]
["221HV-6008","节子洗涤器平衡水阀","稀黑液",25,10,"304L",89,400,10,1000,"BAL",25,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",{"$f":"H12","v":400},null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6010","节子洗涤器集渣阀","节子",150,10,"304L",89,400,176,965,"BAL",150,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",{"$f":"H13","v":400},null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6012","节子洗涤器排渣阀","节子",150,10,"304L",89,400,176,965,"BAL",150,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",400,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6015","节子洗涤器冲洗水阀","稀黑液",25,10,"304L",89,400,10,1000,"BAL",25,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",400,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6103","浆渣洗涤器集渣阀","尾浆",150,10,"304L",89,400,176,965,"BAL",150,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",400,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6104","浆渣洗涤器平衡水阀","滤液",25,10,"304L",89,400,40,1000,"BAL",25,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",400,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6106","浆渣洗涤器冲洗水阀","稀黑液",25,10,304,89,400,40,1000,"BAL",25,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",400,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6107","浆渣洗涤器排渣阀","尾浆",150,10,"304L",89,400,176,965,"BAL",150,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",400,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6111","除砂器1平衡水阀","稀黑液",25,10,304,89,300,20,1000,"BAL",25,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",300,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6114","除砂器1排气阀","稀黑液",25,10,304,89,300,20,1000,"BAL",25,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",300,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6116","除砂器2平衡水阀","稀黑液",25,10,304,89,300,20,1000,"BAL",25,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",300,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["221HV-6119","除砂器2排气阀","稀黑液",25,10,304,89,300,20,1000,"BAL",25,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",300,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6303","EOP段喂料中浓泵、真空泵密封水阀","密封水",25,10,304,25,550,32,1000,"BAL",25,16,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",550,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6310","EOP段喂料立管过氧化氢开关阀","过氧化氢",25,10,"316L",25,"700",3.1,1099,"BAL",25,16,"316L","316L","316L","F","FC","PN.",{"$nulls":3},1,1,"IN","700",null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6319","蒸汽浆料加热器蒸汽阀1","中压蒸汽",65,25,"316L",210,1200,"2.3t/h",6.4,"BAL",65,25,"316L","316L","316L","F","FC","PN.",{"$nulls":3},1,1,"IN",1200,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6320","蒸汽浆料加热器蒸汽阀2","中压蒸汽",65,25,"316L",210,1200,"2.3t/h",6.4,"BAL",65,25,"316L","316L","316L","F","FC","PN.",{"$nulls":3},1,1,"IN",1200,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6333","蒸汽浆料加热器蒸汽阀3","中压蒸汽",65,25,"316L",210,1200,"2.3t/h",6.4,"BAL",65,25,"316L","316L","316L","F","FC","PN.",{"$nulls":3},1,1,"IN",1200,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6334","蒸汽浆料加热器蒸汽阀4","中压蒸汽",65,25,"316L",210,1200,"2.3t/h",6.4,"BAL",65,25,"316L","316L","316L","F","FC","PN.",{"$nulls":3},1,1,"IN",1200,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6324","Eop段氧气加入器氧气开关阀","氧气",25,25,304,25,1400,"1.5Nm3/h",4.17,"BAL",25,25,"316L","316L","316L","F","FC","PN.",{"$nulls":3},1,1,"IN",1400,null,"C","脱脂处理","A",null,"HV-001-DCS-JB-JB-XX","已提取",8,2410308]
["241HV-6325","Eop段化学品混合器出口阀","EOP段浆",250,25,"316L",110,1500,1000,965,"BAL",250,25,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",1500,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6341","Eop反应塔布料器进料阀1","EOP段浆",200,25,"316L",110,1500,250,965,"BAL",200,25,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",1500,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6342","Eop反应塔布料器进料阀2","EOP段浆",200,25,"316L",110,1500,250,965,"BAL",200,25,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",1500,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6343","Eop反应塔布料器进料阀3","EOP段浆",200,25,"316L",110,1500,250,965,"BAL",200,25,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",1500,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6344","Eop反应塔布料器进料阀4","EOP段浆",200,25,"316L",110,1500,250,965,"BAL",200,25,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",1500,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]
["241HV-6345","Eop反应塔卸料器密封水阀控制","密封水",15,25,304,25,1550,2,1000,"BAL",15,25,"316L","316L","316L","F","FI","PN.",{"$nulls":3},1,1,"IN",1550,null,"C",null,"A",null,"HV-001-DCS-JB-JB-XX",null,8]

{"sheet":"调节阀 (技术)","index":3,"n_rows":44,"n_cols":35,"rows_kept":44,"merged":[[8,2,8,9],[8,10,8,19],[8,20,8,22],[8,23,8,27]]}
{"$rows_empty":8}
[null,null,"Process Data\n工艺参数 ",{"$nulls":7},"Valve Information\n阀门信息",{"$nulls":9},"Flow Data\n流量参数 (m3/h)",null,null,"Pressure Data\n压力参数 (KPa(g))"]
["Tag No.","Application","Medium","Size\nmm","Class\nPN","Pipe\nMater.","Temp.\n℃","Press.\nKPa(g)","Flow\nm3/h","Dens.\nKg/dm3","Valve\nType","Size\nmm","Class\nPN","Body\nMater.","Spool\nMater.","Seat\nMater.","Conn.Type","Fail\nType","Act.\nType","Posit.\nType","Min.    \nFlow","Norm.\nFlow","Max.\nFlow","Inlet\nPress.","Max.\ndP","Norm.\ndP","Min.\ndP","dP\nColsed","Sup.","Remarks","Rev.","回路图编号"]
["仪表位号","应 用","介质","管径","压力\n等级","管道\n材质","温度","压力","流量","密度","类型","口径","压力\n等级","阀体\n材质","阀芯\n材质","阀座\n材质","连接\n形式","故障\n类型","执行器\n类型","定位器\n类型","最小\n流量","正常\n流量","最大\n流量","进口\n压力","最大\n压差","正常\n压差","最小\n压差","关断\n压差","供货","备注","版本"]
["221LCV-6005","节子洗涤器液位调节阀","尾浆",250,10,"304L",86,300,465,965,"SEV",250,16,"316L","316L","316L","F","FI","PN.","EP",139.63963963963963,465,558,{"$f":"H12","v":300},50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221HCV-6006","筛选喂料泵来浆稀释调节阀","稀黑液",100,10,"304L",89,400,104,1000,"SEV",100,16,"316L","316L","316L","BF","FI","PN.","EP",31.23123123123123,104,124.8,{"$f":"H13","v":400},50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221FCV-6014","节子洗涤器稀释调节阀","稀黑液",150,10,"304L",89,400,176,1000,"SEV",150,16,"316L","316L","316L","BF","FI","PN.","EP",52.85285285285285,176,211.2,400,50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221PCV-6017","压力除节机进浆压力调节阀","粗浆",350,10,"304L",89,"300",900,965,"SEV",300,16,"316L","316L","316L","F","FI","PN.","EP",750,900,1080,"300",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,10]
["221FCV-6020","压力除节机尾浆出口流量调节阀","尾浆",150,10,"304L",89,"240",92,965,"SEV",125,16,"316L","316L","316L","BF","FI","PN.","EP",76.66666666666667,92,110.39999999999999,"240",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221FCV-6021","压力除节机稀释流量调节阀","稀黑液",80,10,"304L",89,"400",50,965,"SEV",80,16,"316L","316L","316L","BF","FI","PN.","EP",41.66666666666667,50,60,"400",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221HCV-6022","压力除节机冲洗流量调节阀","稀黑液",80,10,"304L",89,"400",87,965,"SEV",80,16,"316L","316L","316L","BF","FI","PN.","EP",72.5,87,104.39999999999999,"400",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221FCV-6087","压力除节机、一段压力筛进浆流量调节阀","浆",350,10,"304L",89,"300",1032,965,"SEV",350,16,"316L","316L","316L","F","FI","PN.","EP",860,1032,1238.3999999999999,"300",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,10]
["221FCV-6091","一段压力筛稀释流量调节阀","稀黑液",100,10,"304L",89,"300",90,1000,"SEV",100,16,"316L","316L","316L","BF","FI","PN.","EP",75,90,108,"300",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221FCV-6093","一段压力筛尾浆流量调节阀","尾浆",200,10,"304L",86,330,187,965,"SEV",150,16,"316L","316L","316L","BF","FI","PN.","EP",155.83333333333334,187,224.4,330,50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221FCV-6094","二段压力筛进浆流量调节阀","尾浆",300,10,"304L",86,"300",754,965,"SEV",300,16,"316L","316L","316L","F","FI","PN.","EP",226.42642642642642,754,904.8,"300",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,10]
["221PCV-6095","二段压力筛进浆压力调节阀","浆",350,10,"304L",86,300,596,1000,"SEV",300,16,"316L","316L","316L","F","FI","PN.","EP",null,596,754,300,50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,10]
["221FCV-6098","二段压力筛稀释流量调节阀","稀黑液",80,10,"304L",86,"400",67,1000,"SEV",65,16,"316L","316L","316L","BF","FI","PN.","EP",20.12012012012012,67,80.39999999999999,"400",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221FCV-6100","二段压力筛尾浆流量调节阀","尾浆",150,10,"304L",86,"240",150,965,"SEV",125,16,"316L","316L","316L","BF","FI","PN.","EP",45.04504504504504,150,180,"240",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221LCV-6108","浆渣洗涤器液位调节阀","尾浆",250,10,"304L",86,300,205,965,"SEV",200,16,"316L","316L","316L","BF","FI","PN.","EP",61.56156156156156,205,246,300,50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221FCV-6109","浆渣洗涤器稀释调节阀","稀黑液",150,10,"304L",86,"400",152,1000,"SEV",125,16,"316L","316L","316L","BF","FI","PN.","EP",45.645645645645644,152,182.4,"400",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221PDCV-6115","三段压力筛上浆回流压力调节阀","尾浆",80,10,"304L",86,"300",55,965,"SEV",65,16,"316L","316L","316L","BF","FI","PN.","EP",16.516516516516518,55,66,"300",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221FCV-6120","三段压力筛出浆流量调节阀","尾浆",200,10,"304L",86,"300",464,965,"SEV",200,16,"316L","316L","316L","BF","FI","PN.","EP",139.33933933933935,464,556.8,"300",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221PCV-6121","三段压力筛进浆压力调节阀","尾浆",250,10,"304L",86,"300",464,965,"SEV",250,16,"316L","316L","316L","F","FI","PN.","EP",139.33933933933935,464,556.8,"300",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221FCV-6124","三段压力筛尾浆流量调节阀","尾浆",100,10,"304L",86,"240",130,965,"SEV",100,16,"316L","316L","316L","BF","FI","PN.","EP",39.03903903903904,130,156,"240",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221FCV-6126","三段压力筛稀释流量调节阀","稀黑液",65,10,"304L",86,"400",35,1000,"SEV",65,16,"316L","316L","316L","BF","FI","PN.","EP",10.51051051051051,35,42,"400",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["221HCV-6127","稀释水泵出口调节阀","稀黑液",500,10,"304L",89,420,1000,1000,"SEV",350,16,"316L","316L","316L","F","FI","PN.","EP",300.3003003003003,1000,1200,420,50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,10]
["241HCV-6301","Eop喂料立管下部稀释调节阀","滤液",100,10,"316L",89,400,80,1000,"SEV",80,16,"316L","316L","316L","BF","FI","PN.","EP",66.66666666666667,80,96,400,50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["241HCV-6302","Eop喂料立管上部稀释调节阀","滤液",50,10,"316L",89,400,20,1000,"SEV",50,16,"316L","316L","316L","BF","FI","PN.","EP",16.666666666666668,20,24,400,50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["241HCV-6311","Eop段喂料中浓泵出口调节阀","浆","200/250",25,"316L",86,"1520",1000,965,"SEV","200/250",25,"316L","316L","316L","F","FI","PN.","EP",833.3333333333334,1000,1200,"1520",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["241FCV-6314","进Eop喂料立管氢氧化钠流量调节阀","氢氧化钠",40,10,"304L",25,"700",{"v":4.2,"d":"4"},1340,"SEV",40,16,"316L","316L","316L","BF","FI","PN.","EP",3.5000000000000004,4.2,5.04,"700",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["241FCV-6315","进Eop喂料立管过氧化氢流量调节阀","过氧化氢",25,10,"316L",25,"700",{"v":3.1,"d":"3"},1099,"SEV",25,16,"316L","316L","316L","BF","FI","PN.","EP",2.5833333333333335,3.1,3.7199999999999998,"700",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["241FCV-6316","蒸汽浆料加热器蒸汽总管流量调节阀","中压蒸汽",125,25,"20#",210,1200,"9.1t/h",{"v":6.4,"d":"6"},"SEV",100,25,"316L","316L","316L","BF","FI","PN.","EP","7.6t/h","9.1t/h","11t/h",1200,50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["241FCV-6323","Eop段氧气加入器氧气总管流量调节阀","氧气",25,25,304,25,1400,"1.5Nm3/h",{"v":4.17,"d":"4"},"GLO",25,25,"316L","316L","316L","BF","FI","PN.","EP","1.25Nm3/h","1.5Nm3/h","1.8Nm3/h",1400,50,30,20,null,"C","脱脂处理","A","CV-001-DCS-JB-JB-XX",null,8]
["241HCV-6330","Eop反应塔顶部滤液阀","滤液",80,16,"316L",89,400,55,1000,"SEV",80,16,"316L","316L","316L","BF","FI","PN.","EP",45.833333333333336,55,66,400,50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["241PCV-6331","Eop反应塔顶部压力调节阀","浆",250,16,"316L",86,"500",1000,965,"SEV",250,16,"316L","316L","316L","F","FO","PN.","EP",833.3333333333334,1000,1200,"500",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]
["241FCV-6336","Eop喷放塔滤液流量调节","滤液",250,10,"316L",89,"650",460,1000,"SEV",250,16,"316L","316L","316L","F","FI","PN.","EP",383.33333333333337,460,552,"650",50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX","已提取",8,2410328]
["241QCV-6340","Eop喷放塔中浓泵出口浓度","滤液",150,10,"316L",89,650,120,1000,"SEV",125,16,"316L","316L","316L","BF","FI","PN.","EP",43,120,150,650,50,30,20,null,"C",null,"A","CV-001-DCS-JB-JB-XX",null,8]